SEWAGE FLOW RATE ESTIMATING GUIDE

(Range and Typical are shown in gallons per unit)

Estimates are based on US standards for water usage and sewage strength.

## Typical Wastewater Flow Rates from Commercial Sources

| Source | Unit | Range | Typical |
| --- | --- | --- | --- |
| Airport | Passenger | 2-4 | 3 |
| Auto Service Station | Vehicle Served | 7-13 | 10 |
|  | Employee | 9-15 | 12 |
| Bar | Customer | 1-5 | 3 |
|  | Employee | 10-16 | 13 |
| Department Store | Toilet Room | 400-600 | 500 |
|  | Employee | 7-13 | 10 |
| Industrial Building | Employee | 7-16 | 13 |
| (Sanitary Waste Only) |  |  |  |
| Laundry (Self-Serve) | Machine | 450-650 | 550 |
|  | Wash | 45-55 | 50 |
| Office | Employee | 7-16 | 13 |
| Restaurant | Meal | 2-4 | 3 |
| Shopping Center | Employee | 7-13 | 10 |
|  | Parking Space | 1-2 | 2 |

## Typical Wastewater Flow Rates from Residential Sources

| Source | Unit | Range | Typical |
| --- | --- | --- | --- |
| Apartment, High-Rise | Person | 35-75 | 50 |
| Low Rise | Person | 50-80 | 65 |
| Hotel | Guest | 30-55 | 45 |
| Individual Residence |  |  |  |
| Typical Home | Person | 45-90 | 70 |
| Better Home | Person | 60-100 | 80 |
| Luxury Home | Person | 75-150 | 95 |
| Older Home | Person | 30-60 | 45 |
| Summer Cottage | Person | 25-50 | 40 |
| Motel |  |  |  |
| with Kitchen | Unit | 90-180 | 100 |
| without kitchen | Unit | 75-150 | 95 |
| Mobile Home Park | Person | 30-50 | 40 |

## Typical Wastewater Flow Rates from Institutional Sources

| Source | Unit | Range | Typical |
| --- | --- | --- | --- |
| Hospital, Medical | Bed | 125-240 | 155 |
|  | Employee | 5-15 | 10 |
| Hospital, Mental Health | Bed | 75-140 | 100 |
|  | Employee | 5-15 | 10 |
| Correctional Institution (Prison) | Inmate | 75-150 | 115 |
|  | Employee | 5-15 | 10 |
| Rest Home | Resident | 50-120 | 85 |
| School, day |  |  |  |
| w/ cafeteria, gym, & showers | Student | 15-30 | 25 |
| w/ cafeteria only | Student | 10-20 | 15 |
| no cafeteria; no gym | Student | 5-17 | 11 |
| School, boarding | Student | 50-100 | 75 |

## Typical Wastewater Flow Rates from Recreational Sources

| Source | Unit | Range | Typical |
| --- | --- | --- | --- |
| Apartment, Resort | Person | 50-70 | 60 |
| Cabin, Resort | Person | 8-50 | 40 |
| Cafeteria | Customer | 1-3 | 2 |
|  | Employee | 8-12 | 10 |
| Campground (developed) | Person | 20-40 | 30 |
| Cocktail Lounge | Seat | 12-25 | 20 |
| Coffee Shop | Customer | 4-8 | 6 |
|  | Employee | 8-12 | 10 |
| Country Club | Member Present | 60-130 | 100 |
|  | Employee | 10-15 | 13 |
| Day Camp (no meals) | Person | 10-15 | 13 |
| Dining Hall | Meal Served | 4-10 | 7 |
| Dormitory | Person | 20-50 | 40 |
| Hotel, Resort | Person | 40-60 | 50 |
| Store, Resort | Customer | 1-4 | 3 |
|  | Employee | 8-12 | 10 |
| Swimming Pool | Customer | 5-12 | 10 |
|  | Employee | 8-12 | 10 |
| Theatre | Seat | 2-4 | 3 |
| Visitor Center | Visitor | 4-8 | 5 |